## Quadro de cargas
[5 empty] | Cargas de Iluminação |  |  |  | CARGAS DE FORÇA (tomadas elétricas)
[9 empty] | Tomadas de uso geral (TUG) |  |  | Tomadas de Uso especial (TUE) |  |  | Potência total do circuito (W) | Corrente de Projeto (A) | FCT | FCA | Comprimento do circuito | Corrente corrigida (A) | seção do condutor (mm²) | Disjutor de proteção (A) | Fase (RST)
Circuito | Função | Cômodo | Área (m2) | Perímetro (m) | Qtde. | potência unitária (W) | potência total (W) ambiente | potência total (W) circuito | Qtde. | potência unitária (W) | potência total (W) | Qtde. | potência unitária (W) | potência total (W)
1 | Chuveiro 1 | Banheiro 1 | 0 | 0 | [6 empty] | 0 | 1 |  | 0 | 0 | 0 | 1.06 | 1 |  | 0 | 6 | 32 | R
2 | [10 empty] | 0 | 1 |  | 0 | 0 | 0 | 1.06 | 1 |  | 0 | 6 | 32 | S
3 | [10 empty] | 4000 | 2 |  | 0 | 4000 | 18.1818 | 1.06 | 1 |  | 17.1527 | 6 | 32 | T
4 | [10 empty] | 1300 |  |  |  | 1300 | 5.9091 | 1.06 | 0.7 |  | 7.9637 | 2.5 | 16 | R
5 | [10 empty] | 1300 |  |  |  | 2600 | 11.8182 | 1.06 | 0.7 |  | 15.9275 | 2.5 | 16 | S
1300
0
6 | [10 empty] | 0 |  |  |  | 0 | 0 | 1.06 | 0.7 |  | 0 | 2.5 | 16 | T
0
7 | [10 empty] | 0 |  |  |  | 0 | 0 | 1.06 | 0.7 |  | 0 | 2.5 | 16 | R
8 | [10 empty] | 0 |  |  |  | 0 | 0 | 1.06 | 0.7 |  | 0 | 2.5 | 16 | S
0
9 | [11 empty] | 1 |  | 0 | 0 | 0 | 1.06 | 1 |  | 0 | 10 | 40 | T
10 | [6 empty] | 0 | 0 | [7 empty] | 0 | 1.06 | 0.7 |  | 0 | 1.5 | 10 | R
0
0
0
0
0
0
11 | [6 empty] | 0 | 0 | [7 empty] | 0 | 1.06 | 0.7 |  | 0 | 1.5 | 10 | S
0
0
0
0
12 | [6 empty] | 0 | 0 | [7 empty] | 0 | 1.06 | 1 |  | 0 | 1.5 | 10 | S
|  | TOTALIZAÇÃO | [12 empty] | 7900 | 35.9091 |  |  |  | 41.0439
[19 empty] | Potência | 9029.6496

## Maquinas
Máquina | Alimentação | Especificações
Printer YSP10 | Single-phase AC 200 to 230V +/-20V | https://global.yamaha-motor.com/business/smt/printer/ysp10/spec/
Conveyor | 220 VAC / 60Hz / Monofásico 120W | https://www.allpoint.com.br/transportador-de-inspecao-e-conexao.html
Panasonic pick and place AM100 | 3-phase AC 200 / 220 V ±10 V, AC 380 / 400 / 420 / 480 V ±20 V 2.0 kVA | https://na.panasonic.com/us/factory-equipment-solutions/electronics-assembly-manufacturing-technologies/surface-mount-technology-smt/am100-single-beam-single-head-placement
Reflow oven Point reflow 12 zonas | 5 linhas, 3 fases 380V 50/60Hz 68kW | https://www.allpoint.com.br/forno-de-refusao-point-reflow-12-zonas.html
Wave solder tnw33-36ex/et | AC220V±10% -50/60Hz-3φ 34kVA 95A | https://www.tamuracorp.com/products/electronic_chemicals/category/fa_systems/w_solder/tnw.html
AOI | 100-120 V, 16A / 200-240V, 8A Single Phase | https://www.vitrox.com/vision-technology-machine-system/optical-inspection-system-aoi-v510i-se-spec.php
Bancada de uso geral | 220V - 1980W
Item | Potência (W)
Computador + monitor 21" | 300
Hot air station | 1000
Soldering station | 80
Misc | 500
Iluminação | 100
Total | 1980

## Alimentador
| Potência (W) | Fator de demanda | Potência final
Demanda iluminação | 0 | 0.59 | 0
Demanda tomadas | 9029.6496 | 0.24 | 2167.1159
Demanda chuveiros | 0 | 1 | 0
Demanda carregador EV | 0 | 1 | 0
|  | Total | 2167.1159
|  | Corrente | 3.2926
|  | Condutor | 16mm²
|  | Diâmetro condutor | 5.1
|  | qtde | 4
|  | área ocupada | 81.7104
|  | Tamanho eletroduto | 1
|  | área | 506.6925
|  | % ocupada | 16.13%

## Cômodos
Cômodo | Área | Perímetro | Iluminação (min) | Tomadas (min)

## Parâmetros
Tensão | 220
FCT | 1.06
trifásico | 380

## Cabos
chrome-extension://efaidnbmnnnibpcajpcglclefindmkaj/https://www.guiadaengenharia.com/wp-content/uploads/2019/02/tabelas-completas-5410.pdf